## NEC Rules
Motor HP | NEC 430-150 460V FLA | Durr Fuse Sizes | NEMA Starter Size | 430-52(c)(1) Maximum NEC Fuse or Breaker Size | 430-22(a) Wire Size | Minimum Ground Conductor Size | Maximum Circuit Length (ft.) | Standard Fuse Size LookUp Table |  | Current | Wire Size | Current | Ground Size | RoundDown Fuse Size LookUp Table |  | Standard Disconnect Size LookUp Table |  | Standard Transformer Size LookUp Table |  | Nearest Fuse Size LookUp Table
0.5 | 1.1 | 1.8 | 1 | 2 | 12 | 14 | 4157 |  | 1 | 0 | 12 | 0 | 14 | 1 | 1 | 0 | 30 | 0 | 1000 |  | 1
0.75 | 1.6 | 2.5 | 1 | 3 | 12 | 14 | 2969 | 1 | 1.25 | 25 | 10 | 15 | 12 | 3 | 3 | 30 | 60 | 1000 | 1500 | 1.125 | 1.25
1 | 2.1 | 3.2 | 1 | 4 | 12 | 14 | 2309 | 1.25 | 1.6 | 35 | 8 | 20 | 10 | 6 | 6 | 60 | 100 | 1500 | 2000 | 1.425 | 1.6
1.5 | 3 | 5 | 1 | 5.6 | 12 | 14 | 1599 | 1.6 | 1.8 | 50 | 6 | 30 | 10 | 10 | 10 | 100 | 200 | 2000 | 3000 | 1.7 | 1.8
2 | 3.4 | 5.6 | 1 | 6 | 12 | 14 | 1223 | 1.8 | 2 | 65 | 4 | 40 | 10 | 15 | 15 | 200 | 400 | 3000 | 5000 | 1.9 | 2
3 | 4.8 | 7.5 | 1 | 9 | 12 | 14 | 866 | 2 | 2.25 | 85 | 3 | 60 | 8 | 20 | 20 | 400 | 600 | 5000 | 7500 | 2.125 | 2.25
5 | 7.6 | 12 | 1 | 15 | 12 | 14 | 547 | 2.25 | 2.5 | 100 | 2 | 100 | 6 | 25 | 25 | 600 | SUB | 7500 |  | 2.375 | 2.5
7.5 | 11 | 17.5 | 1 | 20 | 12 | 14 | 378 | 2.5 | 2.8 | 115 | 1 | 200 | 4 | 30 | 30 | 1200 | SUB |  |  | 2.65 | 2.8
10 | 14 | 25 | 1 | 25 | 12 | 12 | 297 | 2.8 | 3 | 130 | 1/0 | 300 | 3 | 35 | 35 | 3000 |  |  |  | 2.9 | 3
15 | 21 | 35 | 2 | 40 | 10 | 10 | 314 | 3 | 3.2 | 150 | 2/0 | 400 | 2 | 40 | 40 |  |  |  |  | 3.1 | 3.2
20 | 27 | 45 | 2 | 50 | 10 | 10 | 378 | 3.2 | 3.5 | 175 | 3/0 | 500 | 1 | 45 | 45 |  |  |  |  | 3.35 | 3.5
25 | 34 | 60 | 2 | 60 | 8 | 10 | 300 | 3.5 | 4 | 200 | 4/0 | 600 | 1/0 | 50 | 50 |  |  |  |  | 3.75 | 4
30 | 40 | 70 | 3 | 75 | 6 | 10 | 404 | 4 | 4.5 | 230 | 250 | 800 | 2/0 | 60 | 60 |  |  |  |  | 4.25 | 4.5
40 | 52 | 80 | 3 | 100 | 4 | 8 | 310 | 4.5 | 5 | 255 | 300 | 1000 | 3/0 | 70 | 70 |  |  |  |  | 4.75 | 5
50 | 65 | 100 | 3 | 125 | 4 | 8 | 391 | 5 | 5.6 | 285 | 350 | 1200 | 4/0 | 80 | 80 |  |  |  |  | 5.3 | 5.6
60 | 77 | 125 | 4 | 150 | 3 | 8 | 514 | 5.6 | 6 | 310 | 400 | 1600 | 250 | 90 | 90 |  |  |  |  | 5.8 | 6
75 | 96 | 150 | 4 | 175 | 1 | 6 | 509 | 6 | 6.25 | 335 | 500 | 2000 | 350 | 100 | 100 |  |  |  |  | 6.125 | 6.25
100 | 124 | 200 | 4 | 225 | 2/0 | 6 | 583 | 6.25 | 7 | 380 | 600 | 2500 | 400 | 110 | 110 |  |  |  |  | 6.625 | 7
125 | 156 | 250 | 5 | 275 | 3/0 | 6 | 556 | 7 | 7.5 | 420 | 700 |  |  | 125 | 125 |  |  |  |  | 7.25 | 7.5
150 | 180 | 275 | 5 | 325 | 4/0 | 4 | 570 | 7.5 | 8 | 460 | 750 |  |  | 150 | 150 |  |  |  |  | 7.75 | 8
200 | 240 | 400 | 5 | 450 | 350 | 3 | 561 | 8 | 9 | 475 | 800 |  |  | 175 | 175 |  |  |  |  | 8.5 | 9
250 | 302 | 500 | 6 | 600 | 500 | 3 |  | 9 | 10 | 490 | 900 |  |  | 200 | 200 |  |  |  |  | 9.5 | 10
300 | 361 | 600 | 6 | 700 | 700 | 2 |  | 10 | 12 | 520 | 1000 |  |  | 225 | 225 |  |  |  |  | 11 | 12
350 | 414 | 700 | 6 | 800 | 900 | 1 |  | 12 | 15 | 545 | 1250 |  |  | 250 | 250 |  |  |  |  | 13.5 | 15
400 | 477 | 800 | 6 | 1000 | 1500 | 1 |  | 15 | 17.5 | 590 | 1500 |  |  | 300 | 300 |  |  |  |  | 16.25 | 17.5
450 | 515 | 800 | 7 | 1000 | 1750 | 1/0 |  | 17.5 | 20 | 625 | 1750 |  |  | 350 | 350 |  |  |  |  | 18.75 | 20
500 | 590 | 1000 | 7 | 1200 | 2000 | 1/0 |  | 20 | 25 | 650 | 2000 |  |  | 400 | 400 |  |  |  |  | 22.5 | 25
[8 empty] | 25 | 30 | 665 |  |  |  | 450 | 450 |  |  |  |  | 27.5 | 30
Use this table for 460 volt motors in a 480 volt system, with NEMA starters and Class R fuses. | [7 empty] | 30 | 35 |  |  |  |  | 500 | 500 |  |  |  |  | 32.5 | 35
[8 empty] | 35 | 40 |  |  |  |  | 600 | 600 |  |  |  |  | 37.5 | 40
[8 empty] | 40 | 45 |  |  |  |  | 700 | 700 |  |  |  |  | 42.5 | 45
SIZING GUIDELINES (NEC Article Reference) | [7 empty] | 45 | 50 |  |  |  |  | 800 | 800 |  |  |  |  | 47.5 | 50
[8 empty] | 50 | 60 |  |  |  |  | 1000 | 1000 |  |  |  |  | 55 | 60
Ampacity and Motor Rating Determination 430-6(a)(1) | [7 empty] | 60 | 70 |  |  |  |  | 1200 | 1200 |  |  |  |  | 65 | 70
This section states that cable ampacities shall be from NEC 310-15(b) Table or (c) calculated & Motor Amps shall be per NEC Tables 430-147 to 150 | [7 empty] | 70 | 75 |  |  |  |  | 1600 | 1600 |  |  |  |  | 72.5 | 75
[8 empty] | 75 | 80 |  |  |  |  | 2000 | 2000 |  |  |  |  | 77.5 | 80
Individual Motor Feeds (430-22): | [7 empty] | 80 | 85 |  |  |  |  | 2500 | 2500 |  |  |  |  | 82.5 | 85
Branch circuit conductors shall have an ampacity of not less than 125% of the motors full load current rating as determined by Section 430-6(a)(1): | [7 empty] | 85 | 90 |  |  |  |  | 3000 | 3000 |  |  |  |  | 87.5 | 90
[8 empty] | 90 | 100 |  |  |  |  | 4000 | 4000 |  |  |  |  | 95 | 100
Motor Overload Sizing (430-32): | [7 empty] | 100 | 110 | [10 empty] | 105 | 110
Motors with a marked service factor not less than 1.15 |  |  |  |  | 125% | Name Plate FLA |  | 110 | 125 |  |  |  |  | 5000 | 5000 |  |  |  |  | 117.5 | 125
Motors with a marked temperature rise not over 40 °C |  |  |  |  | 125% | Name Plate FLA |  | 125 | 150 |  |  |  |  | 6000 | 6000 |  |  |  |  | 137.5 | 150
All other motors |  |  |  |  | 115% | Name Plate FLA |  | 150 | 175 | [10 empty] | 162.5 | 175
[8 empty] | 175 | 200 | [10 empty] | 187.5 | 200
Individual Motor Fuses (430-52(c)(1) & Table 430-152): | [7 empty] | 200 | 225 | [10 empty] | 212.5 | 225
A protective device that has a rating or setting not exceeding the value calculated according to the values given in Table 430-152 shall be used. | [7 empty] | 225 | 250 | [10 empty] | 237.5 | 250
The NEC Maximum is 175% of NEC FLA, rounded up to nearest manufacturer's fuse size. Durr standard is 150% of NEC FLA of motor, rounded up to nearest manufacturer's fuse size. | [7 empty] | 250 | 275 | [10 empty] | 272.5 | 275
[8 empty] | 275 | 300 | [10 empty] | 287.5 | 300
Main Disconnect Fuses (430-62): | [7 empty] | 300 | 325 | [10 empty] | 312.5 | 325
The nearest fuse to the Largest motor fuse (175% of NEC FLA) + Sum of NEC FLAs of other loads, but not less then 125% of Largest motor NEC FLA + 125% of Heating load + the Sum of the other NEC FLA. Also not less then 115% of the Sum of all NEC FLA. All fuse sizes are based on maximum permitted values as listed in table 430-152. (175% of largest motor NEC FLA + NEC FLA of other equipment in panel) | [7 empty] | 325 | 350 | [10 empty] | 337.5 | 350
[8 empty] | 350 | 400 | [10 empty] | 372.5 | 400
Main Disconnect (430-110(2)): | [7 empty] | 400 | 450 | [10 empty] | 425 | 450
At least 115% of the Sum of FLA of all loads. | [7 empty] | 450 | 500 | [10 empty] | 475 | 500
[8 empty] | 500 | 600 | [10 empty] | 550 | 600
Main Panel Feeds (430-24): | [7 empty] | 600 | 700 | [10 empty] | 650 | 700
125% of Main Disconnect Fuse, but not larger than Main Disconnect switch. | [7 empty] | 700 | 800 | [10 empty] | 750 | 800
Note: Client specifications may require sizing the panel feed to the capacity of the bus plug. | [7 empty] | 800 | 1000 | [10 empty] | 900 | 1000
[8 empty] | 1000 | 1200 | [10 empty] | 1100 | 1200
[8 empty] | 1200 | 1600 | [10 empty] | 1400 | 1600
[8 empty] | 1600 | 2000 | [10 empty] | 1800 | 2000
[8 empty] | 2000 | 2500 | [10 empty] | 2250 | 2500
[8 empty] | 2500 | 3000 | [10 empty] | 2750 | 3000
[8 empty] | 3000 | 4000 | [10 empty] | 3500 | 4000
[8 empty] | 4000 | 5000 | [10 empty] | 4500 | 5000
5000

## Device VA'S
Power Consumption in VA
Manufacturer | DEVICE | VA | VOLTAGE
AB | 1771-IAD | 16 | 120VAC
AB | 1771-IAD | 16 | 120VAC
AB | 1771-OAD | 17 | 120VAC
AB | 1771-P7 (PLC I/O RACK POWER SUPPLY) | 176 | 120VAC
AB | 1771-P4S (PLC I/O RACK POWER SUPPLY) | 89 | 120VAC
AB | 1794-ASB (Flex ASB ) | 10.8 | 24VDC
AB | 1794-IA16 (Flex Input Card) | 35 | 120VAC
AB | 1794-IE4XOE2 (Flex Combo Analog Card) | 4 | 24VDC
AB | 1794-OA16 (Flex Output Card) | 4.7 | 120VAC
AB | 1794-OW8 (Flex Iso Card) | 5.5 | 24VDC
AB | 1794-IE8 (Flex Analog Input Card) | 3 | 24VDC
AB | 1794-OE4 (Flex Analog Output Card) | 4.5 | 24VDC
AB | 2711-K9C1 (PANELVIEW 900) | 110
AB | 509-BOD (MOTOR STARTER SIZE 1) | 30
AB | 509-COD (MOTOR STARTER SIZE 2) | 30
AB | 509-DOD (MOTOR STARTER SIZE 3) | 45
AB | 509-EOD (MOTOR STARTER SIZE 4) | 70
AB | 509-FOD (MOTOR STARTER SIZE 5) | 100
AB | 700-P400A1 (NEMA CONTROL RELAY) | 20
AB | 800T-PT16X (NEMA PILOT LIGHT) | 5
AB | 855T-B10YL3 (ALARM STACKLIGHT) | 72
AB | CONTACTOR 110A | 64
AB | CONTACTOR 24A | 7
AB | SMC 97A | 75
Sola | 24VDC POWER SUPPLY, 2.5A | 156 | 120VAC
Asco | PILOT VALVE SOLENOID | 40
Asco | VENT VALVE SOLENOID | 43
Dayton | PC COOLING FAN | 30
Dongan | AO6-SA6 (IGNITION TRANSFORMER) | 175
Dungs | VDK2200-S02 (Valve Pressure Proving System) | 80
Eagle | OVEN PURGE TIMER | 11
Eclipse | Safety-Shutoff Valve Opening VA | 159
Edwards | ALARM HORN | 15
Honeywell | C7061 (Flame Detector) | 7
Honeywell | MODULATING GAS VALVE MOTOR | 40
Honeywell | RM7838B1013 (FLAME SAFETY RELAY) | 15
Honeywell | UDC1000 (HIGH TEMP LIMIT) | 6
LMI | C731 Metering Pump | 360
LMI | C771 Metering Pump | 720
LMI | M151 Metering Pump | 360
Maxon | Safety-Shutoff Valve Opening VA | 240
PILZ | Safety Relay | 11 | 120VAC
Redlion | CUB3T100 (ELAPSED TIME METER) | 1
Siemens | 3RT101 (Control Relay) | 3.5 | 120VAC
Siemens | 3RT102 (Contactor .5 to 15HP) | 7.5 | 120VAC
Siemens | 3RT103 (Contactor 16 to 30 HP) | 14.2 | 120VAC
Siemens | 3RT1044 (Contactor 40 to 50HP) | 20 | 120VAC
Siemens | 3RT1045/6 (Contactor 60 to 75HP) | 21 | 120VAC
Siemens | 3TF5011 (Contactor 100HP) | 39 | 120VAC
Siemens | 3SB02-TT1 (IEC PTT PILOT LIGHT) | 2.5 | 120VAC
Siemens | 8WD4308 (ALARM STACKLIGHT) | 35 | 120VAC
ATC | 405A100F2X Plug In Timer | 1.2 | 120VAC
Veris | H-321 (Current Transmitter 2 Wire) | 0.5
Veris | H-720 (Current Transmitter 3 Wire) | 0.5
Effector | SY0100 (Flow Monitor) | 3 | 120VAC
GIC | Temperature Transmitter | 0.5 | 24VDC
| Modulating Valve | 0.5 | 24VDC
Asco | Seal Water Solenoid Valve | 40 | 120VAC
| Spray Bypass Valve Actuator | 45 | 24VDC
Effector | Pressure Switch | 3 | 120VAC
Siemens | 5136-DNS-200S (DeviceNet I/O Rack Adapter) | 12 | 24VDC
Siemens | 6ES7138-4CB10-0AB0 (DeviceNet I/O Rack Power Module, 24VDC) | 0.06 | 24VDC
Siemens | 6ES7138-4CB00-0AB0 (DeviceNet I/O Rack Power Module, 120VAC) | 0.06 | 120VAC
Siemens | 6ES7131-4EB00-0AB0 (DeviceNet I/O Rack 2DI Module, 120VAC) | 0.72 | 120VAC
Siemens | 6ES7131-4BD00-0AB0 (DeviceNet I/O Rack 4DI Module, 24VDC) | 0.24 | 24VDC
Siemens | 6ES7132-4FB00-0AB0 (DeviceNet I/O Rack 2DO Module, 120VAC, 1A) | 2.16 | 120VAC
Siemens | 6ES7132-4HB00-0AB0 (DeviceNet I/O Rack 2DO Module, Contact, 5A) | 1.2 | 24VDC/230VAC
Siemens | 6ES7131-4BD00-0AA0 (DeviceNet I/O Rack 4DO Module, 24VDC, 0.5A) | 0.48 | 24VDC
Siemens | 6ES7132-4BD30-0AA0 (DeviceNet I/O Rack 4DO Module, 24VDC, 2A) | 0.72 | 24VDC
Siemens | 6ES7134-4GB00-0AB0 (DeviceNet I/O Rack 2AI Module, 4-20mADC) | 1.92 | 24VDC
Siemens | 6ES7134-4NB00-0AB0 (DeviceNet I/O Rack 2AI Module, Type K T/C) | 0.72 | 24VDC
Siemens | 6ES7134-4JB50-0AB0 (DeviceNet I/O Rack 2AI Module, RTD) | 0.72 | 24VDC
Siemens | 6ES7135-4GB00-0AB0 (DeviceNet I/O Rack 2AO Module, 4-20mADC) | 3.6 | 24VDC
Siemens | 6EP1536-2AA00 (24VDC Power Supply, 20A, 600VAC in) | 756 | 600VAC

## Power Loads
Panel 2000
Directions: 1. Save file as "Panel XXXX Design" where XXXX equals the panel number. 2. Provide Panel Name and Number at top of worksheet. 3. Provide total resistive heat load in amps at 480VAC. 4. Provide PLC transformer size in VA's. 5. Provide motor descriptions and Horse Power (Largest motor first). 6. Provide all information on Panel VA worksheet.
Bus Plug/PDP Feeder | 400
Bus Plug/PDP Feeder Fuse | 400 |  | Main Fuse NEC Rules
Main Disconnect | 400 |  | 430-62 |  |  | 424-3 | 115% FLA
Main Disconnect Fuse Size | 350 |  | 324.8167 | 325 | 325 | 325 | 350
Panel NEC FLA | 294.8375 |  | Actual | Larger | Nearest
Resistive Heat Load (Amps)
24VDC Power Supply(Amps) | 10
Transformer Size (VA) | 5000
Motor Description | HP | NEC FLA | Durr Fuse | Starter | Pwr Wire | Gnd Wire
Entrance air seal fan | 7.5 | 11 | 17.5 | 1 | 12 | 14 |  | 3RA1125-1JA24-1AK6
#1 Heater unit recirc. fan | 20 | 27 | 45 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6
#1 Heater unit recirc. fan | 20 | 27 | 45 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6
Heater ventilation fan | 2 | 3.4 | 5.6 | 1 | 12 | 14 |  | 3RA1125-1EA23-1AK6
#2 Heater unit recirc. fan | 20 | 27 | 45 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6
#2 Heater unit recirc. fan | 20 | 27 | 45 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6
Aggitation air | 7.5 | 11 | 17.5 | 1 | 12 | 14 |  | 3RA1125-1JA24-1AK6
Oven ventilation fan | 7.5 | 11 | 17.5 | 1 | 12 | 14 |  | 3RA1125-1JA24-1AK6
Exit air seal fan | 7.5 | 11 | 17.5 | 1 | 12 | 14 |  | 3RA1125-1JA24-1AK6
Cooling Fan 1 | 20 | 27 | 45 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6
Cooling Fan 2 | 20 | 27 | 45 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6
Cooling Fan 3 | 20 | 27 | 45 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6
Cooling Fan 4 | 20 | 27 | 45 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6
Cooling Fan 5 | 15 | 21 | 35 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6
Cooling Fan 6 | 15 | 21 | 35 | 2 | 10 | 10 |  | 3RA1135-4BB33-1AK6

## Panel 120VAC VA
Panel 2000
Max Transformer Primary Fuse | 7
Transformer Size | 2000
Max Transformer Secondary Fuse | 25
Total Circuit Amps | 0 | 0 |  | 0 |  | 0
Total Connected VA | 0 | 0 |  | 0 |  | 0
|  | 2102CB |  | 2104CB |  | 2106CB
DEVICE | VA | QTY | Total | QTY | Total | QTY | Total
24VDC POWER SUPPLY, 10A | 250 |  | 0 |  | 0 |  | 0
C7061 (Flame Detector) | 7 |  | 0 |  | 0 |  | 0
Safety-Shutoff Valve Opening VA | 240 |  | 0 |  | 0 |  | 0
MODULATING GAS VALVE MOTOR | 40 |  | 0 |  | 0 |  | 0
RM7838B1013 (FLAME SAFETY RELAY) | 15 |  | 0 |  | 0 |  | 0
Spray Bypass Valve Actuator | 45 |  | 0 |  | 0 |  | 0
3SB02-TT1 (IEC PTT PILOT LIGHT) | 2.5 |  | 0 |  | 0 |  | 0
3RH11 (Control Relay AC) | 3.5 |  | 0 |  | 0 |  | 0
|  |  | 0 |  | 0 |  | 0

## Panel 24VDC VA
Panel 2000
Max Power Supply Primary Fuse | 5
24VDC Power Supply Size (Amps) | 20
Max Transformer Secondary Fuse | 20
Total Circuit Amps | 2.3625 | 0.475 |  | 0.28583 |  | 1.6017
Total Connected VA | 56.7 | 11.4 |  | 6.86 |  | 38.44
|  | 3002CB |  | 3004CB |  | 3006CB
DEVICE | VA | QTY | Total | QTY | Total | QTY | Total
6ES7138-4CB10-0AB0 (Power Mod, 24VDC) | 0.06 |  | 0 | 1 | 0.06 | 2 | 0.12
6ES7134-4JB50-0AB0 (2AI Module, RTD) | 0.72 |  | 0 | 3 | 2.16 |  | 0
6ES7134-4NB00-0AB0 (2AI Module, Type K T/C) | 0.72 |  | 0 |  | 0 |  | 0
6ES7135-4GB00-0AB0 (2AO Module, 4-20mADC) | 3.6 |  | 0 |  | 0 |  | 0
6ES7131-4BD00-0AB0 (4DI Module, 24VDC) | 0.24 |  | 0 | 6 | 1.44 |  | 0
6ES7131-4BD00-0AA0 (4DO Module, 24VDC, 0.5A) | 0.48 |  | 0 |  | 0 | 4 | 1.92
3RH11 (Control Relay DC) | 3.2 | 2 | 6.4 | 1 | 3.2 | 2 | 6.4
3RT102 (Contactor .5 to 15HP) | 7.5 |  | 0 |  | 0 |  | 0
3RT103 (Contactor 16 to 30 HP) | 14.2 |  | 0 |  | 0 |  | 0
3RT104 (Contactor 40 to 60HP) | 20 |  | 0 |  | 0 |  | 0
3SB02-TT1 (IEC PTT PILOT LIGHT) | 2.5 | 2 | 5 |  | 0 | 6 | 15
UDC2500 (HIGH TEMP LIMIT) | 6 |  | 0 |  | 0 |  | 0
Alarm Horn | 15 |  | 0 |  | 0 | 1 | 15
|  |  | 0 |  | 0 |  | 0

## Air Conditioner Calc
Panel 2000
Control Panel Heat Load Calculations
Contractor: |  |  | Durr Systems |  |  | Panel # | E211
Project: |  |  | Detroit Diesel |  |  | Date: | 2006-10-19
1. Gross Sheet Metal Surface Area
|  | H = |  | 84.12 | Height (Inches)
|  | W = |  | 78.5 | Width (Inches)
|  | D = |  | 18.125 | Depth (Inches)
|  | GSM = |  | 12.3238 | Gross Sheet Metal Area (Square Meters)
2. Free Sheet Metal Surface Area
Free Sheet metal Surface Area (FSM) = GSM minus all surface area in contact with a wall or floor or covered/obstructed by components (transformers, OIT displays, pilot lights, etc.)
|  |  |  | 5% | Percent Of Top Surface Area Obstructed
|  |  |  | 100% | Percent Of Bottom Surface Area Obstructed
|  |  |  | 0% | Percent Of Back Surface Area Obstructed
|  |  |  | 5% | Percent Of Front Surface Area Obstructed
|  |  |  | 0% | Percent Of Right Side Surface Area Obstructed
|  |  |  | 0% | Percent Of Left Side Surface Area Obstructed
|  | FSM = |  | 11.1469
3. Ambient Control Panel Temperature
For panels on the plant floor use 30o Celsius, panels on a balcony or mezzanine use 40o Celsius. If the actual ambient is higher than 30o or 40o Celsius, use the actual temperature.
|  | Ta = |  | 30 | Ambient Temperature (Degrees Celsius)
4. Maximum Control Panel Operating Temperature
For panels containing PLC equipment, VFDs, or other electronic equipment 50o Celsius. All other panels use 60o Celsius.
|  | Tmax = |  | 50 | Maximum Operating Temperature (Degrees Celsius)
5. Heat Dissipation Capacity
|  | Pd = |  | 1226.1587 | Heat Dissipation Capacity (Watts)
6. Control Panel Heat Load
This is the total of all heat loads inside the panel from the attached work sheets.
|  | Pl = |  | 3214.1 | Heat Load (Watts)
7. Heat Dissipation Deficiency
|  | Pr = |  | 1987.9413 | Heat Dissipation Deficiency (Watts)
8. Result |  |  | 6779 BTU of cooling is required for this control panel.

## Magnetic Heat Load
MAGNETICS HEAT LOAD WORKSHEET
|  |  |  | Heat Disipation | Heat Disipation
Quantity | Description | Part Number | Manufacturer | Each (Watts) | Total (Watts)
1 | DC Power Supply | 6EP1536-2AA00 | Siemens | 60 | 60
| DC Power Supply | SDN4-24-100 | Sola | 12 | 0
| Oven Purge Timer | HP50-133 | Eagle | 12.95 | 0
| Alarm Horn | 871P-G1 | Edwards |  | 0
3 | Pilot Light | XB4BW | Telemecanique | 2.5 | 7.5
| UDC 2500 | DC100L | Honeywell | 4 | 0
| Timer | 405A100F1X | ATC | 1.2 | 0
| Flame Relay | RM7838C1012 | Honeywell | 10 | 0
| AC Control Relay | CA2DN | Telemecanique | 0.945 | 0
5 | DC Control Relay | CA3DN | Telemecanique | 3.2 | 16
| Safety Relay | PNOZX9P | Pilz |  | 0
| 3RA11, 0.5HP | 3RA1125-0JA23-1AK6 | Siemens | 0.5 | 0
| 3RA11, 0.75HP | 3RA1125-0KA23-1AK6 | Siemens | 0.5 | 0
| 3RA11, 2HP | 3RA1125-1EA23-1AK6 | Siemens | 0.9 | 0
| 3RA11, 7.5HP | 3RA1125-1JA24-1AK6 | Siemens | 1.6 | 0
| 3RA11, 10HP | 3RA1135-4AB33-1AK6 | Siemens | 1.8 | 0
| 3RA11, 15HP | 3RA1135-4BB33-1AK6 | Siemens | 1.8 | 0
| 3RA11, 40HP | 3RA1135-4HB36-1AK6 | Siemens | 2.6 | 0
| 3RA11, 0.75HP | 3RT1036-1BB40 | Siemens | 5 | 0
| 3RA11, 0.75HP | 3RT1044-1BB40 | Siemens | 4.6 | 0
| 3RA11, 0.75HP | 3RT1045-1BB40 | Siemens | 7.7 | 0
| 3RA11, 0.75HP | 3RT1046-1BB40 | Siemens | 10.8 | 0
| 3 Pole MSP, 0.75HP, 0.9-1.25A | 3RV1021-0KA10 | Siemens | 6 | 0
| 3 Pole MSP, 1HP, 1.1-1.6A | 3RV1021-1AA10 | Siemens | 6 | 0
| 3 Pole MSP, 1.5HP, 1.8-2.5A | 3RV1021-1CA10 | Siemens | 6 | 0
| 3 Pole MSP, 2HP, 2.2-3.2A | 3RV1021-1DA10 | Siemens | 6 | 0
| 3 Pole MSP, 3HP, 2.8-4.0A | 3RV1021-1EA10 | Siemens | 6 | 0
| 3 Pole MSP, 5HP, 4.5-6.3A | 3RV1021-1GA10 | Siemens | 6 | 0
| 3 Pole MSP, 10HP, 7.0-10A | 3RV1021-1JA10 | Siemens | 7 | 0
| 3 Pole MSP, 10HP, 9.0-12.5A | 3RV1021-1KA10 | Siemens | 7 | 0
| 3 Pole MSP, 20HP, 14.0-20.0A | 3RV1021-4BA10 | Siemens | 8 | 0
| 3 Pole MSP, 25HP, 18-25A | 3RV1031-4DB10 | Siemens | 12 | 0
| 3 Pole MSP, 30HP, 22-32A | 3RV1031-4EB10 | Siemens | 15 | 0
| 3 Pole MSP, 40HP, 28-40A | 3RV1031-4FB10 | Siemens | 20 | 0
| 3 Pole MSP, 50HP, 36-50A | 3RV1042-4HB10 | Siemens | 20 | 0
| 3 Pole MSP, 60HP, 45-63A | 3RV1042-4JB10 | Siemens | 20 | 0
| 3 Pole MSP, 75HP, 57-75A | 3RV1042-4KB10 | Siemens | 30 | 0
| 3 Pole MSP, 100HP, 70-90A | 3RV1042-4LB10 | Siemens | 30 | 0
| Shoe w/ Main Breaker, 100A | FBCB100M-HB | Siemens | 30 | 0
| Shoe w/ Main Breaker, 125A | FBCB125M-HB | Siemens | 40 | 0
1 | Shoe w/ Main Breaker, 150A | FBCB150M-HB | Siemens | 40 | 40
| Shoe w/ Main Breaker, 175A | FBCB175M-HB | Siemens | 40 | 0
| Shoe w/ Main Breaker, 200A | FBCB200M-HB | Siemens | 50 | 0
| Shoe w/ Main Breaker, 225A | FBCB225M-HB | Siemens | 50 | 0
| Shoe w/ Main Breaker, 250A | FBCB250M-HB | Siemens | 50 | 0
| Main Breaker, 300A | HLD63M300 | Siemens | 60 | 0
| Main Breaker, 350A | HLD63M350 | Siemens | 60 | 0
| Main Breaker, 400A | HLD63M400 | Siemens | 60 | 0
| Main Breaker, 450A | HLD63M450 | Siemens | 70 | 0
| Main Breaker, 500A | HLD63M500 | Siemens | 70 | 0
| Main Breaker, 600A | HLD63M600 | Siemens | 80 | 0
4 | Circuit Breaker, 1-Pole, UP TO 10A | 5SJ41 SERIES | Siemens | 0.2 | 0.8
| Transformer, 500VA | 9070EO51D101E23 | Square D | 32.24 | 0
5 | Line Reactor (110A) | RL-08003 | MTE | 92 | 460
5 | MM440 VFD (15HP) | 6ES6440-2UD33-7EA1 | Siemens | 522 | 2610
0
0
0
0
0
0
0
|  |  |  | Total Magnetic Heat Load | 3194.3
Note: | 1. No heat loads for terminals, disconnects, fuses, or power distribution blocks.
2. Add any internally mounted devices at the bottom of the work sheet.

## PLC Heat Load
PLC HEAT LOAD WORKSHEET
|  |  |  | Heat Disipation | Heat Disipation
Quantity | Description | Part Number | Manufacturer | Each (Watts) | Total (Watts)
1 | DeviceNet I/O Rack Adapter | 5136-DNS-200S | Siemens | 2 | 2
3 | DeviceNet I/O Rack Power Module, 24VDC | 6ES7138-4CB10-0AB0 | Siemens |  | 0
| DeviceNet I/O Rack Power Module, 120VAC | 6ES7138-4CB00-0AB0 | Siemens |  | 0
0
| DeviceNet I/O Rack 2DI Module, 120VAC | 6ES7131-4EB00-0AB0 | Siemens | 0.2 | 0
6 | DeviceNet I/O Rack 4DI Module, 24VDC | 6ES7131-4BD00-0AB0 | Siemens | 0.8 | 4.8
| DeviceNet I/O Rack 2DO Module, 120VAC, 1A | 6ES7132-4FB00-0AB0 | Siemens | 4 | 0
| DeviceNet I/O Rack 2DO Module, Contact, 5A | 6ES7132-4HB00-0AB0 | Siemens | 0.6 | 0
| DeviceNet I/O Rack 4DO Module, 24VDC, 0.5A | 6ES7131-4BD00-0AA0 | Siemens | 0.8 | 0
4 | DeviceNet I/O Rack 4DO Module, 24VDC, 2A | 6ES7132-4BD30-0AA0 | Siemens | 2.8 | 11.2
3 | DeviceNet I/O Rack 2AI Module, 4-20mADC | 6ES7134-4GB00-0AB0 | Siemens | 0.6 | 1.8
| DeviceNet I/O Rack 2AI Module, Type K T/C | 6ES7134-4NB00-0AB0 | Siemens | 0.6 | 0
| DeviceNet I/O Rack 2AI Module, RTD | 6ES7134-4JB50-0AB0 | Siemens | 0.6 | 0
| DeviceNet I/O Rack 2AO Module, 4-20mADC | 6ES7135-4GB00-0AB0 | Siemens | 2 | 0
0
0
| Control Logix Power Supply, 24VDC | 1756-PB75 | Allen Bradley | 22 | 0
| Control Logix Power Supply, 120VAC | 1756-PA75 | Allen Bradley | 20 | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
|  |  |  | Total PLC Heat Load | 19.8
Note: | 1. No heat loads for PLC, RIO adapters, E-NET cards or any other rack powered card.
2. Add any internally mounted devices at the bottom of the work sheet.

## Equip
| Starters | Dim | Watts | Qty | total Watts | Additional
0.5 | 3RA1125-0JA23-1AK6 | 55X295X175 | 11.5 | 2 | 23
0.75 | 3RA1125-0KA23-1AK6 |  | 11.5 | 2 | 23
2 | 3RA1125-1EA23-1AK6 |  | 11.5 | 1 | 11.5
7.5 | 3RA1125-1JA24-1AK6 |  | 11.5 | 2 | 23
10 | 3RA1135-4AB33-1AK6 | 70X330X180 | 15 | 2 | 30 | 3RT1946-4GA0T line side terminal kit
15 | 3RA1135-4BB33-1AK6 |  | 15 | 2 | 30
40 | 3RA1135-4HB36-1AK6 |  | 15 | 2 | 30
Relays
| 3RH1131-1AB00 | 45x57.5X72 | 3.2