## Sheet1
Volvo Japan - Conveyor System Electrical Controls Issues
ITEM | DESCRIPTION | Comments
1 | Remove the HMI from conveyor control provide one additional stand-alone HMI with 100V power plug and one Profi-Net plug. | waiting for Volvo Japan reply, cost and drawing approval
2 | Additional 100V power for each stand-alone HMI (3) must be powered and wired from the conveyor control panel | waiting for Volvo Japan reply, cost and drawing approval
3 | Additional Profi-Net plug in each stand-alone HMI (3) must be connected (wired) to conveyor Profi-Net comm system | waiting for Volvo Japan reply, cost and drawing approval
4 | Provide solenoid valve for paint kitchen compressed air supply piping, 24VDC if possible, normally closed powered open | waiting for Volvo Japan reply, cost and drawing approval
5 | Wire compressed air solenoid into process equipment control valve emergency stop (E-Stop) circuit. | waiting for Volvo Japan reply, cost and drawing approval
6 | Paint Kitchen exhaust fan needs to be wired so it will operate 24 hours a day. It will be powered and controlled from the process control panel and manually started and stopped from a pushbutton control station at the paint kitchen location | waiting for Volvo Japan reply, cost and drawing approval
7 | Add 1 local conveyor “Take IN/OUT” manual control station. Operators to include: o lift table up PB o lift table down PB o lift tale forward PB o lift table reverse PB o OUT lift table auto/manual SS o IN lift table auto manual SS | waiting for Volvo Japan reply, cost and drawing approval
8 | QEPP system interlocks | Cybernetik will provide as part of "Scope of Supply"
9 | PLC programusing STEP 7 Version 5.4 | Cybernetik will provide as part of "Scope of Supply"
10 | HMI programming using WinCC 2008 | Cybernetik will provide as part of "Scope of Supply"
11 | Safety Relays - Pilz in lieu of Rockwell | waiting for Volvo Japan reply
12 | Safety Light Curtain - Sick in lieu of P&F | waiting for Volvo Japan reply
13 | Photo Sensor - IFM in lieu of P&F | waiting for Volvo Japan reply
14 | Prox Sensor - IFM in lieu of P&F | waiting for Volvo Japan reply
15 | Customers Design Review (Electrical_CV) wk1215 | Reviewed
16 | Customers Design Review (Electrical_CV) wk1216 | Reviewed
17 | Robot Interlocks as per attached email | waiting for Volvo Japan reply
18 | Conveyor control panel customer approval | waiting for Volvo Japan reply
19 | Conveyor control BOM customer approval | waiting for Volvo Japan reply
20 | Conveyor pushbutton station customer approval | waiting for Volvo Japan reply
21 | Process control panel customer approval | waiting for Volvo Japan reply
22 | Process control BOM customer approval | waiting for Volvo Japan reply
23 | Paint Kitchen operator station customer approval | waiting for Volvo Japan reply, cost and drawing approval
24 | QEPP PLC and HMI programs to Cybernetik | PMPF working on this
25